Evaporative Cooler

Engineering Specification								5/98

1.0 	General.  The evaporative cooling module shall be self-contained.  It will consist 	of the component parts as listed in the following sections.

1.1	Quality Assurance.

The manufacturer shall:

A. 	Furnish proof satisfactory to the owner or his representative, of 				having manufactured evaporative cooler systems for a period of 				not less than five years.

B.	Make its facility available to the owner or his representative for 				quality control audit without prior notification.

1.2	Submittals.

The manufacturer shall:

A.	Submit product data, including dimensions, service connections, 				accessories, controls with schematics and sequence of operation, electrical 			nameplate data, and evaporative media data.

B.	Furnish rigging, assembly, installation and maintenance instructions.

C.	Furnish operation and maintenance manuals, including required 				descriptive vendor literature and parts listings.

2.0	Acceptable Manufacturers.

The evaporative cooling module will be manufactured by AbsolutAire, Inc., 	Kalamazoo, MI,  or an approved equal.

3.0 	Cooling components.

3.1	The evaporative cooler casing will be minimum (18) (16) gauge aluminized steel, 	welded to structural steel framing.  All exterior seams are to be 100% weather 	tight.  All interior surfaces will be cleaned of all oil and grease.  Painted exterior 	will consist of a high quality prime coat and a finish coat of industrial enamel with 	rust inhibitors.  Exterior color is to be selected by owner or his representative.

3.2	The evaporative cooler sump tank will be minimum (16) (14) gauge 304 stainless 	steel, the interior of which will be protected with an asphalt-based coating.

3.3	The evaporative cooler sump pump will be piped, wired, and fully assembled at 	the manufacturer's facility.

3.4	The evaporative cooler media shall consist of (6") (12") (18") thick Munters 	(CelDek®) (GlasDek®) media sized at a maximum face velocity of 600 fpm.

Optional: 2" thick distribution pad manufactured from the same material as the 	evaporative media for uniform water distribution throughout the media thickness.

Optional: 4" thick PVC drift eliminator to remove entrained water droplets from 	the leaving air side of the cooling media.  Cooling media shall be easily removed 	for servicing and replacement.

3.5	The evaporative cooler module will also contain a float valve and switch, and 	labeled overflow, bleed, fill, and drain connections.  A service panel shall permit 	easy access to the pump, float, and water regulating valve.

3.6	The evaporative cooler piping shall be schedule 40 (pvc) (copper), completely 	assembled and leak tested at the manufacturer's facility.

3.7	The evaporative cooler will include a submersible pump, UL. listed, hermetically 	sealed, dielectric oil-filled and with Buna-N seal.  Horsepower rating of pump 	shall be conducive to the flow rate required and piping system installed.  Pump to 	centrifugal type with strainer to prevent intake of solid material.  The pump shall 	be 120/1/60 voltage.  Pump shall discharge into a heavy-duty (pvc) (copper) 	distribution header.  This header will have orifices of a size and quantity to 	adequately distribute water over and through the evaporative media.  A water 	regulator valve shall be installed in the distribution network to permit field 	adjustment of water flow over the media.

s:\evapspec.doc